PLEASE NOTE: The following specification contains areas, highlighted with the [ ] symbol. In these areas, the engineer has to make a selection, add specific, project related information and has to delete what is not applicable for the specific project.

Chlorine Dioxide Amperometric Sensor

On-line, single-channel industrial sensor that measures chlorine dioxide in drinking water treatment plants, distribution networks, and other applications that require monitoring ClO2 at the ppb and ppm levels.

The instrument uses an amperometric method to measure ClO2 concentration. A membrane allows the selective

diffusion of ClO2 molecules to the amperometric sensor. The measurement is compensated for temperature. The sensor

requires a digital universal controller.

Technical Data

Measuring range	0 - 2 mg/L ClO2

Detection limit	0.01 mg/L ClO2

Accuracy	5 % or ±10 ppb ClO2, whichever is greater

Standard deviation	1.5 %

Response time	90 % in less than 90 seconds

Measuring interval	Continuous

Flow	14 L/h (200 - 250 mL/min) auto-regulated by flow through cell

Pressure range	0.1 - 2 bar in flow cell

Sample temperature	2 - 45 °C

Temperature compensation

Automatic over sample temperature range

Measuring principle	Amperometric/Membrane (electrode, membrane, electrolyte)

Interferences	None

Calibration method	Zero Calibration: Electrically or with ozone-free water

Calibration: Comparison of lab method with process sample

Calibration interval	2 months

Mounting	Flat, vertical surface (panel, stand, etc.)

Sample input	0.25” outer diameter Sample output	0.5” inner diameter Storage conditions	-20 °C - 60 °C

Relative humidity	0 - 90 % non-condensing

Maintenance interval   6 months for membrane and electrolyte (measurement cell)

Height                            270 mm Width                             250 mm Weight                           6.5 kg

Enclosure waterproof rating

Controller compatibility

IP66 / NEMA 4X

Universal controller, Multi-parameter universal controller

Scope of delivery

[ ] (delete what is not needed) Analytical Instrument

Chlorine Dioxide Amperometric Sensor

Optional Accessories

[ ] Acidification unit

[ ] Intermittent flow unit

[ ] Instrument stand

[ ] 125 V Power cord with strain relief

[ ] 230 V Power cord with strain relief

[ ] Digital extension cable  	(select 1/7.6/15.2/30.5 m) (Standard cable length is 0.4 m)

[ ] Digital termination box (required when the length of cable between the digital sensor and controller is between 100 and 1000 m)

Replacement Parts

[ ] Chlorine dioxide electrode

[ ] Pre-mounted membranes (pk/4) [ ] Electrolyte

Services

[ ] Manufacturer’s services to perform start-up on instrument to include basic operational training and certification of

performance of the instrument.

[ ] Manufacturer’s Service Agreement that covers all the manufacturer’s recommended preventative maintenance, regularly scheduled calibration and any necessary repairs beginning from the time of equipment start-up through to end user acceptance / plant turnover and the first 12 months of end-user operation post turnover.

Brand:	Hach

Product:	9187 sc Chlorine Dioxide Amperometric Sensor