Sludge Level Probe

Probe for monitoring the level or depth (height from the tank floor or depth of the water surface) of a sludge blanket. The method of measuring the sludge level will be by ultrasonic pulse directed toward the sludge blanket in the tank. The measurement is without contact between the probe and the sludge. The probe defines the sludge blanket based on user-selected sludge concentration or “blanket threshold”. It is equipped with an exchangeable magnetic coupled wiper

that cleans the probe. A position sensor that also compensates for angle when the probe is not mounted exactly vertically is placed in the sensor. The probe automatically compensates for temperature. A visual performance LED indicator light indicates proper performance. The probe is factory calibrated. The probe automatically detects deterioration of disrupted sedimentation. It senses the ultrasonic echo return with the information of the separation layer independent of density.

The probe requires a universal digital controller.

Includes the capability to remotely monitor sensors on any browser-enabled device and present diagnostics on the overall health of the measurements (on predictive diagnostics-enabled sensors), as well as upcoming and required maintenance - reducing user risk and downtime.

Technical Data

Measuring principle Measuring range Resolution Accuracy

Operating temperature range

Pressure range

Power requirements (Voltage)

Response time Flow

Mounting

configurations Calibration method Material Certifications Dimensions (D x L) Weight

Cable length

Controller

Ultrasonic measurement

0.2 - 12 m sludge level

0.03 m sludge level

0.1 m

0 - 50 °C

≤ 0.3 bar or ≤ 3 m

12 V, 2.4 W, provided by Digital Controller

10 to 1800 s adjustable

Max. 3 m/s (the presence of air bubbles affects the measurement)

Fixed pole mount, pivot mount or chain mount

One-off on commissioning, automatic

POM; wiper magnet encapsulating compound: epoxy resin; wiper rubber: silicone rubber

CE

185 mm x 130 mm

3.5 kg

10 m (optional extension cables available)

Universal Controller, Multi-Parameter Universal Controller

PLEASE NOTE: The following specification contains areas, highlighted with the [ ] symbol. In these areas, the engineer has to make a selection, add specific, project related information and has to delete what is not applicable for the specific project.

Scope of delivery

[ ] (delete what is not needed)

Analytical Instrument

Sludge level probe

Accessories

[ ] Set of wiper blades

[ ] Wiper arm, magnetic driven

[ ] Adjusting screw for wiper arm [ ] Impact protection

[ ] Extension pipe 1.0 m with new flange including screw set [ ] Extension pipe 1.8 m with new flange including screw set [ ] Probe chain stay

[ ] Diagnostic software without interface cable

[ ] Diagnostic software with Universal digital controller interface cable

[ ] Diagnostic software with multi-parameter universal digital controller interface cable

Mounting Hardware

[ ] Tank rim fixing, made of stainless steel

[ ] Pivot mounting, 0.35 m pipe [ ] Pivot mounting, 1 m pipe

[ ] Rail mounting assembly, made of stainless steel

Services

[ ] Manufacturer’s services to perform start-up on instrument to include basic operational training and certification of

performance of the instrument.

[ ] Manufacturer’s Service Agreement that covers all the manufacturer’s recommended preventative maintenance, regularly scheduled calibration and any necessary repairs beginning from the time of equipment start-up through to end user acceptance / plant turnover and the first 12 months of end-user operation post turnover.

Brand:

Hach

Product:

Sonatax sc Sludge Level Probe