PLEASE NOTE: The following specification contains areas, highlighted with the [ ] symbol. In these areas, the engineer has to make a selection, add specific, project related information and has to delete what is not applicable for the specific project.

UV Fluorescence Sensor for Oil in Water

Process probe for continuous measurement of PAH (polycyclic aromatic hydrocarbons ) in water which show a strong correlation to the content of oil in water. The method of measuring oil in water will be an ultraviolet (UV) fluorescence analysis. Measured is the intensity of radiation from a sample which absorbs light at a shorter wavelength and emits light at a longer wavelength (fluorescence).

PAHs are the integral parts of most mineral oil products and thus a very specific indicator of oil contamination in water. Different kinds of oils show different radiation characteristics. The measurement values can be converted to reflect the total oil content for mineral oils.

The sensor is factory calibrated and needs no calibration prior to use. The sensor requires a universal digital controller. A

version with stainless steel and one with titanium for aggressive media is available.

Technical Data

UV Oil in Water Sensor, low range

Measurement method	UV fluorescence method for polycyclic aromatic hydrocarbons (PAH)

Measuring range	0 - 50 ppb (µg/L) and 0 - 500 ppb (µg/L) PAH

0.1 - 1.5 ppm (mg/L) and 0.1 - 15 ppm (mg/L) Oil with calibration standard

UV Oil in Water Sensor, high range

Measurement method	UV fluorescence method for polycyclic aromatic hydrocarbons (PAH)

Measuring range	0 - 500 ppb (µg/L) and 0 - 5,000 ppb (µg/L) PAH

0.1 - 15 ppm (mg/L) and 0.1 - 150 ppm (mg/L) Oil with calibration standard

UV Oil in Water Sensor (in general, all ranges)

Light source	Miniature xenon flashlamp with interference filter

Detector	UV photodiode with interference filter; Compensation of daylight and flashlamp intensity fluctuations

Excitation	Wavelength 254 nm Wavelength	Measurement: 360 nm Detection limit	1.2 µg/L PAH (in pure water)

Resolution	0.1 ppb (µg/L) (PAH) in the lowest measuring range Reproducibility	2.5 % of measured value at constant temperature (PAH) Response time	10 s (T90)

Calibration	Factory calibrated with UV fluorescence standard or process calibration with results of a grab sample analysis.

pH value(s)	≥ 4

Available with

Cleaning System

Mounting

configurations

Yes

Immersion, Inline, or Bypass

Material	Housing: stainless steel 316Ti (1.4571) or titanium

Controller compatibility

Universal Controller, Multi-Parameter Universal Controller

Sample temperature	1 - 40 °C

Ambient temperature	-5 - 45 °C

Pressure range	Probe: 30 bar max.

Flow cell: 1 bar max.

Safety installation fitting: 5 bar max.

Dimensions	68 x 306 mm (D x L; without connector and suspension pin)

Weight	Stainless steel: 2.8 kg

Titanium: 1.8 kg

Safety Armature for Inline Installation

Pipe connection	DN65, PN16

Pressure range	< 6 bar

Weight	18 kg without probe

Max. length (driven out probe)

Approx. 550 mm

Wetted materials	Ball valve: stainless steel 1.4401, PTFE Armature: stainless steel 1.4571, NBR70

Scope of delivery

[ ] (delete what is not needed) Analytical Instrument

[ ] UV Fluorescence PAH Sensor, stainless steel, 1.5 m cable, low range 0 - 500 ppb (0.1 - 15 ppm Oil) [ ] UV Fluorescence PAH Sensor, stainless steel, 10 m cable, low range 0 - 500 ppb (0.1 - 15 ppm Oil)

[ ] UV Fluorescence PAH Sensor, stainless steel, 1.5 m cable, high range 0 - 5000 ppb (0.1 - 150 ppm Oil) [ ] UV Fluorescence PAH Sensor, stainless steel, 10 m cable, high range 0 - 5000 ppb (0.1 - 150 ppm Oil)

[ ] UV Fluorescence PAH Sensor, titanium, 1.5 m cable, low range 0 - 500 ppb (0.1 - 15 ppm Oil) [ ] UV Fluorescence PAH Sensor, titanium, 10 m cable, low range 0 - 500 ppb (0.1 - 15 ppm Oil)

[ ] UV Fluorescence PAH Sensor, titanium, 1.5 m cable, high range 0 - 5000 ppb (0.1 - 150 ppm Oil) [ ] UV Fluorescence PAH Sensor, titanium, 10 m cable, high range 0 - 5000 ppb (0.1 - 150 ppm Oil)

Cleaning Options

[ ] Air blast cleaning system   	(select: 230/115 V AC)

[ ] Air blast cleaning system cable kit   	(select: 5/10/25 m)

Accessories

[ ] Digital extension cable, with molded plug and coupling  	(select: 5/10/15/20/30 m)

Mounting Hardware

[ ] Mounting hardware as follows:

[ ] Chain mounting assembly kit, stainless steel 1.4571, 5 m chain length

[ ] Flow cell mounting assembly kit for clear water applications (‘’Flow Through’’)

[ ] Safety installation armature, probe adapter to fit-in and -out probe in case of fully filled pipe,   	(select:

stainless steel flange/ carbon steel flange/ without flange)

Services

[ ] Manufacturer’s services to perform start-up on instrument to include basic operational training and certification of performance of the instrument.

[ ] Manufacturer’s Service Agreement that covers all the manufacturer’s recommended preventative maintenance, regularly scheduled calibration and any necessary repairs beginning from the time of equipment start-up through to end user acceptance / plant turnover and the first 12 months of end-user operation post turnover.

Brand:	Hach

Product:	FP360 sc UV Fluorescence Oil-in-Water Sensor